## Sheet1
Specifications
Ducted Split System
Model Number			DS025
Performance
Net Cooling * Total Sensible			Total/Sensible @208-230V
@10°F (minus 12°C) condenser inlet air			4100/3178 BTUH
@40°F (4°C) condenser inlet air			3793/3178 BTUH
@60°F (15°C) condenser inlet air			3485/3075 BTUH
@70°F (21°C) condenser inlet air			3690/3075 BTUH
@80°F (27°C) condenser inlet air			3485/3178 BTUH
@100°F (32°C) condenser inlet air			3178/2768 BTUH
@115°F (46°C) condenser inlet air			2973/2563 BTUH
@122°F (50°C) condenser inlet air			2460/2460 BTUH
Controls
Type			Room mounted non-programmable combination thermostat humidistat
Temperature Accuracy/RH% Accuracy			+/- 1 Deg F / +/- 10% RH
Fan-coil Section
Fan Motor Size			90 Rated Watts
Rated Air Flow (free blow)			236 CFM
Rated Air Flow @ Max allow pressure loss			226 @ 0.10"wc / CFM
Heat (Option)
Type			Electric
Capacity			1000 Watts
Humidifier (Option)
Type			Removeable drip pad with integral fan
Capacity - water temp of 60°F (15°C)Capacity - water temp of 60°F (15°C)Capacity - water temp of 60°F (15°C)Capacity - water temp of 60°F (15°C)			0.42 lbs/hr
Capacity - water temp of 90°F (32°C)			0.97 lbs/hr
Capacity - water temp of 120°F (49°C)			1.11 lbs/hr
Electrical Requirements - Evaporator Section
Power			115 Volts/1 phase/60Hz
Current Draw - Cooling mode			0.8 Amps
Current Draw - Heating mode			9.4 Amps
Minimum Circuit Size (w/heat option)			11.6Amps
Optional Humidifier			0.3 Amps
Cabinet - Evaporator Section
Fan coil construction			Aluminum chassis & UL rated plastic panels
Finish			Gray metal epoxy powder coat/textured PVC Acrylic blend
Weight			35lbs
Length			21.43 inches
Width			16.60 inches
Height			15.56 inches
Condensate Drain			0.5 inches
Condensing Unit			DS025 Cond
Nominal Compressor			3.1 Amps
Fan Motor Size			75 Watts
Rated Air Flow (free blow)			275 CFM
Weight			75 lbs
Enclosure - Condensing Unit
Construction			Aluminum
Finish			Anodized
Width			12 inches
Length			34 inches
Height			26 inches
Electrical Requirements - Condensing Unit
Power			208/230 Volts/1 Phase/60Hz
MCA			4.2 Amps
MOP			8.0 Amps
Agency Approval(s)			ETLc
1. Net cooling capacity at entering temperature and humidity conditions of 57 Deg F (14 Deg C) and 55% RH at rated airflow. Reduce capacity by 3% for each 10% reduction in evaporator airflow.
2. Wine Guardian reserves the right to make changes to this document without prior notice at its sole discretion.
3. All ratings at sea level.
4. All btuh capacity and airflow (CFM) values shown are at tested 230v applied on 208/230v rated units (Condensing units and larger evaporators). If field application allows 208v applied to the units dual rated, you can generally expect 2.5%-3.0% decreases in values shown.
7000 Performance Drive | North Syracuse, New York 13212 USA
help.wineguardian.com www.wineguardian.com | info@wineguardian.com
Rev. 08/2021